# VILPE Sense: Findings and Direction

Vaasa Hackathon 2026, VILPE challenge "Unlocking the Value of Building Data"

Reviewed: the challenge brief, the slides, the Sense guidebook (36 pages), the technical brochure, the site layout, and all 7 sensor data files from the Vantaa warehouse.

# 4 things found in their own data

| # | Finding | Proof |
| --- | --- | --- |
| 1 | VILPE's own recommended alarm cries wolf. Their guidebook says: alarm when RH stays above 90% for 24h. On their warehouse, that would fire 180 times in 16 months, while every roof's mold index is near zero (alarm level is 2.5). | Guidebook p.25 + all 7 files |
| 2 | Green roof 2's fan shows 0 rpm for 12 months straight (May 2025 to May 2026, 97% of readings). Its structure was humid 54% of the time vs 21% for Green roof 1, whose fan ran. | Viherkatto 2 file, rpm column |
| 3 | Some outdoor sensors seem to sit in the sun. At summer midday, Katto 4's outdoor sensor reads about 9°C warmer than the others on the same building. The guidebook says never place it in direct sun. Wrong outdoor reading means wrong fan decisions. | Outdoor T columns, June and July |
| 4 | We only got 7 control unit files, but the site layout shows about 45 leak sensors on that roof. Their data would allow a humidity map. | Site layout PDF |

Important: findings 2 and 3 might have a reason (for example, the fan may have been turned off on purpose as a test). We must ask the VILPE experts before pitching them. If they confirm, it is gold.

# Facts from their documents we can build on

- The brochure itself says the moisture data is valuable when a property is sold, but there is no product for it. That validates the Moisture Passport idea.

- The building owner owns the data and can share it by link. A REST API already exists. So the idea is technically realistic.

- Real costs to quote: a small roof leak repair costs a few thousand euros, the Botniahall roof leaks cost six figures.

- Ramboll study: Sense cuts cooling needs by 12 to 21%. The fan uses only 20 to 30 W.

# What to add to make it stand out

The concept becomes one service with three layers:

- Smart alerts that only fire on real risk, fixing finding 1. This builds trust.

- System health watchdog that catches a stopped fan or badly placed sensor, fixing findings 2 and 3. Nobody else will think of this, and it is useful to VILPE right away.

- Moisture Passport for property sales, plus the insurer view for LocalTapiola. This is the business model.

The pitch line: "We found problems in VILPE's own warehouse data that the current system didn't flag. Here's the service that would have caught them, and how VILPE makes money from it."

# Next step

Once the direction is approved: prepare the questions for the VILPE experts, then package these findings into a proof script and charts that can be shown to others.